## Slide 1: Accessing NI Network Shared Variables from EPICS IOCs
Freddie Akeroyd STFC ISIS Facility, GB

## Slide 2: NI Network Variables
Provided by National Instruments (NI) to simplify data exchange between applications and hardware
Abstracts low level communication protocol
Publish/subscribe system
http://www.ni.com/white-paper/5484/en/

## Slide 3: Hardware to Control
Spin echo system supplied and supported by TU Delft
  NI PXI-express system running LabVIEW RT
System uses NI shared variables for communication between internal components
Need to integrate this “black box” into our EPICS instrument control system
  Requires an agreed interface

## Slide 4: Software Interface
TU Delft are more familiar with LabVIEW than EPICS
  so named SVs are a convenient interface
Could use LabVIEW EPICS I/O server
  but not a full IOC implementation
  run where? On RT “black box” or external system?
  an additional component to start/manage
  non-RT systems require purchasing DSC module

## Slide 5: Shared Variable EPICS support
Uses LabWindow/CVI Network Variable Library
  Runtime support for Windows and Linux
Fully configured via text files
  XML file maps SVs -> asyn driver parameters
Subscribed SV events trigger EPICS DB I/O Intr
  Can use “buffered reader” to limit callback rate
Can also read variable inside an SV struct

## Slide 6: Example Configuration
Associate SV “var” with asyn param “c1”
  <param name="c1" type="float64" access="BR,BW“ netvar="//localhost/example/var" />
Load section “sec1” from XML, associate params with asyn port “nsv” and set 100ms as maximum update rate for buffered readers
  NetShrVarConfigure("nsv", "sec1", "$(TOP)/data/netvarconfig.xml", 100)
See http://epics.isis.stfc.ac.uk/